## Sheet1
<table>
Vacuum Breakers | [5 empty] | <caption style='float:left;font-weight:bold;' >Vacuum Breakers</caption>
Vacuum Breaker, Elevated, Chrome-Plated | V |  |  |  |  | <tr><td>Vacuum Breaker, Elevated, Chrome-Plated</td><td>V</td></tr>
Vacuum Breaker, In-Line | W |  |  |  |  | <tr><td>Vacuum Breaker, In-Line</td><td>W</td></tr>
</table>
<table>
Checkstops (Sold in Pairs) | [5 empty] | <caption style='float:left;font-weight:bold;' >Checkstops (Sold in Pairs)</caption>
Concealed | Straight, ½” IPS | A |  |  |  | <tr><td>Concealed</td><td>Straight, ½” IPS</td><td>A</td></tr>
| Straight, ½” Sweat | C |  |  |  | <tr><td></td><td>Straight, ½” Sweat</td><td>C</td></tr>
| Angled, ½” Sweat | D |  |  |  | <tr><td></td><td>Angled, ½” Sweat</td><td>D</td></tr>
| Angled, with Strainer, ½” IPS | E |  |  |  | <tr><td></td><td>Angled, with Strainer, ½” IPS</td><td>E</td></tr>
Exposed | Straight, ½” IPS, Chrome-Plated | B |  |  |  | <tr><td>Exposed</td><td>Straight, ½” IPS, Chrome-Plated</td><td>B</td></tr>
| Angled, with Strainer, ½” IPS, Chrome-Plated | F |  |  |  | <tr><td></td><td>Angled, with Strainer, ½” IPS, Chrome-Plated</td><td>F</td></tr>
Factory installation of checkstops (Add suffix “X” to checkstop code) Min. order 10 |  | X |  |  |  | <tr><td colspan='2'>Factory installation of checkstops (Add suffix “X” to checkstop code) Min. order 10</td><td>X</td></tr>
</table>
<table>
Suggested Roughness Coefficient "n" for Manning's Formula | [5 empty] | <caption style='float:left;font-weight:bold;' >Suggested Roughness Coefficient "n" for Manning's Formula</caption>
(for site drainage) | [5 empty] | <caption style='float:left;font-weight:bold;' >(for site drainage)</caption>
Materia of pipe | From | To | Used |  |  | <tr><td>Materia of pipe</td><td>From</td><td>To</td><td>Used</td></tr>
Pipes | [5 empty] | <tr><td rowspan='5'>Pipes</td></tr>
Asbestos-cement pipe | 0.011 | 0.015 | 0.013 |  |  | <tr><td>Asbestos-cement pipe</td><td>0.011</td><td>0.015</td><td>0.013</td></tr>
Corrugated metal pipe | 0.022 | 0.02 | 0.024 |  |  | <tr><td>Corrugated metal pipe</td><td>0.022</td><td>0.02</td><td>0.024</td></tr>
Cast iron pipe | 0.011 | 0.015 | 0.013 |  |  | <tr><td>Cast iron pipe</td><td>0.011</td><td>0.015</td><td>0.013</td></tr>
Concrete pipe | 0.011 | 0.015 | 0.013 |  |  | <tr><td>Concrete pipe</td><td>0.011</td><td>0.015</td><td>0.013</td></tr>
Ductile iron (cement lined) | 0.011 | 0.015 | 0.013 |  |  | <tr><td>Ductile iron (cement lined)</td><td>0.011</td><td>0.015</td><td>0.013</td></tr>
Plastic pipe, all kinds | 0.009 | 0.015 | 0.01 |  |  | <tr><td>Plastic pipe, all kinds</td><td>0.009</td><td>0.015</td><td>0.01</td></tr>
Steel pipe | 0.012 | 0.02 | 0.015 |  |  | <tr><td>Steel pipe</td><td>0.012</td><td>0.02</td><td>0.015</td></tr>
Vitrified clay pipe | 0.011 | 0.015 | 0.013 |  |  | <tr><td>Vitrified clay pipe</td><td>0.011</td><td>0.015</td><td>0.013</td></tr>
Ditches (open channels) | [5 empty] | <tr><td>Ditches (open channels)</td><td></td><td></td><td></td></tr>
Paved invert corrugated metal steel pipe |  |  | 0.02 |  |  | <tr><td>Paved invert corrugated metal steel pipe</td><td> </td><td></td><td>0.02</td></tr>
Cast iron, ductile iron, concrete, and steel pipe |  |  | 0.013 |  |  | <tr><td>Cast iron, ductile iron, concrete, and steel pipe</td><td></td><td></td><td>0.013</td></tr>
unpaved corrugated metal steel pipe |  |  | 0.024 |  |  | <tr><td>unpaved corrugated metal steel pipe</td><td></td><td></td><td>0.024</td></tr>
Small plant ditches (no vegetation, fair condition) |  |  | 0.015 |  |  | <tr><td>Small plant ditches (no vegetation, fair condition)</td><td></td><td></td><td>0.015</td></tr>
Main plant ditch (grass, some weeds, fair condition) |  |  | 0.03 |  |  | <tr><td>Main plant ditch (grass, some weeds, fair condition)</td><td></td><td></td><td>0.03</td></tr>
Natural ditches (dense weeds, high as flow depth poor condition) |  |  | 0.12 |  |  | <tr><td>Natural ditches (dense weeds, high as flow depth poor condition)</td><td></td><td></td><td>0.12</td></tr>
</table>
<table>
Flow through Orifice (in USC system) | [5 empty] | <caption>Flow through Orifice (in USC system)</caption>
C | d | p |  | Q |  | <tr><th rowspan='2'>C</th><th rowspan='2'>d</th><th colspan='2'>p</th><th>Q</th></tr>
|  | inch H2O | psi | gpm |  | <tr><th>inch H2O</th><th>psi</th><th>gpm</th></tr>
0.9 | 1 | 1 | 0.03613 | 5.1048 |  | <tr><td>0.9</td><td>1</td><td>1</td><td>0.03613</td><td>5.1047597702223</td></tr>
</table>
<table>
Flow through Orifice (in USC system) | [8 empty] | <caption>Flow through Orifice (in USC system)</caption>
C | d | p |  | Q |  |  |  |  | <tr><th rowspan='2'>C</th><th rowspan='2'>d</th><th colspan='2'>p</th><th colspan='2'>Q</th></tr>
|  | inch H2O | psi | gpm | cf/m |  |  |  | <tr><th>inch H2O</th><th>psi</th><th>gpm</th><th>cf/m</th></tr>
0.9 | 1 | 1 | 0.03613 | 5.1048 | 0.68245 |  |  |  | <tr><td>0.9</td><td>1</td><td>1</td><td>0.03613</td><td>5.1047597702223</td><td>0.682454514735601</td></tr>
</table>
T-thru/coupling | - | 16 | 12 | 12 | 12 | R | T-run |  |  | <tr><td>T-thru/coupling</td><td>-</td><td>16</td><td>12</td><td>12</td><td>12</td><td>R</td><td>T-run</td></tr>
Ball | - | 6 |  |  | 8 | B | Ball |  |  | <tr><td>Ball</td><td>-</td><td>6</td><td></td><td></td><td>8</td><td>B</td><td>Ball</td></tr>
Gate | 7 | 9 | 8 | 8 | 8 | G | Gate |  |  | <tr><td>Gate </td><td>7</td><td>9</td><td>8</td><td>8</td><td>8</td><td>G</td><td>Gate</td></tr>
Globe | 333 | 275 | 330 | 330 | 330 | L | Globe |  |  | <tr><td>Globe </td><td>333</td><td>275</td><td>330</td><td>330</td><td>330</td><td>L</td><td>Globe</td></tr>
Angle | 167 | - | 170 | 170 | 170 | A | Angle |  |  | <tr><td>Angle </td><td>167</td><td>-</td><td>170</td><td>170</td><td>170</td><td>A</td><td>Angle</td></tr>
Swing Check | 83 | - | 133 | 133 | 133 | C | Check |  |  | <tr><td>Swing Check</td><td>83</td><td>-</td><td>133</td><td>133</td><td>133</td><td>C</td><td>Check</td></tr>
Butterfly Va | - | 20 | [7 empty] | <tr><td>Butterfly Va</td><td>-</td><td>20</td><td></td><td></td><td></td><td></td><td></td></tr>
Balancing Valve | - | - | 18 | 18 | [5 empty] | <tr><td>Balancing Valve</td><td>-</td><td>-</td><td>18</td><td>18</td><td> </td><td></td><td></td></tr>
Plug-type cock | - | - | 18 | 18 | 18 | P | Plug / Balancing |  |  | <tr><td>Plug-type cock</td><td>-</td><td>-</td><td>18</td><td>18</td><td>18</td><td>P</td><td>Plug / Balancing</td></tr> | <tr><td>-</td><td>-</td><td>18</td><td>18</td></tr>
Source 1: | International Fuel Code and NFPA 54 adapt the data listed in Table XIV in Piping Handbook, written by Crocker, S. in 1945 and published by McGraw-Hill, Inc.
Source 2: | Posted by the following websites: http://www.aquatext.com/tables/frict-wat.htm
http://www.scribd.com/doc/24752539/Fitting-Equivalent-Length
UPC | Uniform Plumbing Code
UPC | International Plumbing Code
OR |  |  |  | Type A Outlets |  |  | Type B Outlets |  |  | Total Scfm |  | <tr><td>OR</td><td></td><td></td><td></td><td>Type A Outlets</td><td></td><td></td><td>Type B Outlets</td><td></td><td></td><td>Total Scfm</td></tr>
No. | SCMF1 | DF | SCMF2 | No. | DF | SCFM | No. | DF | SCFM |  |  | <tr><td>No.</td><td>SCMF1</td><td>DF</td><td>SCMF2</td><td>No.</td><td>DF</td><td>SCFM</td><td>No.</td><td>DF</td><td>SCFM</td><td></td></tr>
6 | 27 | #NAME? | 9 | 0 | #NAME? | #NAME? | 0 | #NAME? | #NAME? | #NAME? |  | #NAME?
12 | 27 | #NAME? | 18 | 0 | #NAME? | #NAME? | 0 | #NAME? | #NAME? | #NAME? |  | #NAME?
0 | 0 | #NAME? | 0 | 44 | #NAME? | #NAME? | 403 | #NAME? | #NAME? | #NAME? |  | #NAME?
12 | 27 | #NAME? | 18 | 80 | #NAME? | #NAME? | 423 | #NAME? | #NAME? | #NAME? |  | #NAME?

## Sheet2
A = Pipe Cross Section Area (m2) | <li>A = Pipe Cross Section Area (m2)</li>
a = Velocity of sound ( m /s) | <li>a = Velocity of sound ( m /s)</li>
c p = Specific Heat Capacity at Constant pressure (kJ/(kg K)) | <li>c p = Specific Heat Capacity at Constant pressure (kJ/(kg K))</li>
c v = Specific Heat Capacity at Constant Volume (kJ/(kg K)) | <li>c v = Specific Heat Capacity at Constant Volume (kJ/(kg K))</li>
ε = Pipe roughness (m) | <li>ε = Pipe roughness (m)</li>
ε mm = Pipe roughness (mm) | <li>ε mm = Pipe roughness (mm)</li>
D = diameter (m) | <li>D = diameter (m)</li>
f = friction factor | <li>f = friction factor</li>
fT = friction factor (flow in zone of complete turbulence). | <li>fT = friction factor (flow in zone of complete turbulence).</li>
h = Specific Enthalpy (kJ/kg ) | <li>h = Specific Enthalpy (kJ/kg )</li>
k = Thermal Conductivity (W/(m K)) | <li>k = Thermal Conductivity (W/(m K))</li>
r = radius of pipe bend (m) | <li>r = radius of pipe bend (m)</li>
K = f (L/D ) | <li>K = f (L/D )</li>
L = Pipe Length (m) | <li>L = Pipe Length (m)</li>
p = Absolute Pressure N / m2 | <li>p = Absolute Pressure N / m2</li>
Pr = Prantl Number =c p. mu / k (Dimensionless) | <li>Pr = Prantl Number =c p. mu / k (Dimensionless)</li>
Q = Volume flow Rate (m3 /s ) | <li>Q = Volume flow Rate (m3 /s )</li>
q = Heat Input per unit mass ( kJ /kg ) | <li>q = Heat Input per unit mass ( kJ /kg )</li>
R = Gas Constant = R o / M (kJ /(kg.K) | <li>R = Gas Constant = R o / M (kJ /(kg.K)</li>
Re = Reynolds Number = v.ρD/μ | <li>Re = Reynolds Number = v.ρD/μ</li>
t = Temperature (C ) | <li>t = Temperature (C )</li>
T = Absolute Temperature (K) | <li>T = Absolute Temperature (K)</li>
u = Specific Internal Energy (kJ/kg) | <li>u = Specific Internal Energy (kJ/kg)</li>
v =Fluid Velocity (m/s) | <li>v =Fluid Velocity (m/s)</li>
w = Work Output per unit mass (kJ/kg) | <li>w = Work Output per unit mass (kJ/kg)</li>
ρ = Density ( kg /m3 ) | <li>ρ = Density ( kg /m3 )</li>
μ =Fluid Viscosity = (Ns/m2 = Pa s) | <li>μ =Fluid Viscosity = (Ns/m2 = Pa s)</li>
z = Elevation (m ) | <li>z = Elevation (m )</li>
g = gravitational acceleration ( 9.81 m /s2) | <li>g = gravitational acceleration ( 9.81 m /s2)</li>